## Sub-Stations
S.No | Name of Sub-Station | Voltage (KV/KV) | Cap.of T/f in MVA) | % age Loading | Action Plan
1 | 220KV Moga | 220/132 | 100 | 99.23 | With the upgradation of 132KV Talwandi Bhai to 220KV with 1x100MVA,220/66KV T/f, some relief has been provided to 220KV Moga. However further relief shall be provided with additional 1x100MVA,220/132 KV auto T/f (already planned).
|  | 220/132 | 100 | 99.23
|  | 220/132 | 100 | 99.23
2 | 220KV Mansa | 220/66 | 100 | 105.14 | Addl.160MVA,220/66KV ,T/f already been purposed at 220KV S/S Mansa
|  | 220/66 | 100 | 105.14
3 | 220 KV Jhunir | 220/66 | 100 | 109 | Addl.160MVA,220/66KV T/f already purposed at 220KV S/S Jhunir will give relief to 220KV S/S Jhunir.
4 | 220KV Mukatsar | 220/132 | 100 | 98 | Commissioning of 220KVS/S Abohar will give relief to overloading
|  | 220/132 | 100 | 98
|  | 220/132 | 100 | 98
5 | 220KV Sultanpur | 220/132 | 10 | 99 | 1x160MVA,220/66KV T/f has already been planned and under installation . This will reduce loading on both 100MVA,220/132KV transformers at Sultanpur .
|  | 220/132 | 10 | 99
6 | 220KV Hambran | 220/66 | 100 | 99 | Under Consideration
|  | 220/66 | 100 | 99
7 | 220KV Dhandari-1 | 220/66 | 100 | 99 | Addl.100/160MVA,220/66KV ,T/f can not be installed due to fault level constraints. However 66 KV Gaunsgarh has been U/G with 160MVA,220/66KV T/f which can give some relief to the Dhandari.
|  | 220/66 | 100 | 99
8 | 220KV Jagraon | 220/66 | 100 | 95 | Relief can be provided by :- 1) By erecting 66 KV Sudhar/Pakhowal DC link will 0.2Sq"conductor size considerable load of Jagraon can be shifted from Pakhowal where 2nd 100MVAT/f has planned . 2)The U/G of 66 KV Sudhar to 220KV with Suitable 220KV connectivity can be considered. However the case is under consideration.
|  | 220/66 | 100 | 95
9 | 220KV Ferozepur | 220/132 | 100 | 99.23 | Load of 132 KV S/S Ferozshah will be shifted to proposed 220KV S/S Kotkarore which has already been commissioned.
|  | 220/132 | 100 | 99.23
10 | 220KV Mukatsar | 220/132 | 100 | 98 | Commissioning of 220KVS/S Abohar will give relief to overloading
|  | 220/132 | 100 | 98
|  | 220/132 | 100 | 98
11 | 220KV Ferozepur Road Ludhiana | 220/66 | 100 | 99.23 | With the Commissioning of Addl.160MVA T/f at Ferozepur Rd.Ludhiana Overlaoding problem has been solved.
12 | 220KV Rajla | 220/66 | 100 | 98.28 | 66 KV Kakrala near 220KV Rajla has been U/G to 220KV . Therefore considerable load of Rajla will be shifted on Kakrala.

## Lines
S.No | Name of Lines | No. of Ckts. | Conductor size (Sq") | % age Loading | Action Plan
1 | 220KV Moga - BajaKhana | SC | 0.4 | 104.84 | New link from 220KV S/S Baghapurana- BajaKhana line has been planned and will give relief to over loading .
2 | 220KV Sunam-Patran | SC | 0.4 | 99.68 | After commissioning of 220KV Bangan the loading of this line will come down .
3 | 220KV Sahnewal -PGCIL, Ludhiana | SC | 0.4 | 104 | With comissioning of earlier planned network i.e LILO of 1 Ckt LLK2-JGR2,LLK2-SNW2,LLK2-DDK2 ,each at 400KV PGCIL , Ludhiana,this loading will come down .
4 | 220KV Jagraon-400KV Power Grid | SC | 0.4 | 104 | Loading will come down with the LILOof 220KV Jagraon- Moga at Himmatpura.
5 | 220KV Fagan Majra- PTA | DC | 0.4 | 109 | Some relief can be provided with :- 1) Commissioning of 400KV Rajpura & its 220KV,Network 2) Linking of 220KV Nabha -400KV Dhuri All these above works have already been planned
6 | 220KV Malerkotla- Dhuri | DC | 0.4 | 111 | With the commissioning of 400KV Dhuri along with its associated 220KV Network,this loading shal come down .
7 | 220KV Patiala-Rajla-Patran | DC | 0.4 | 111 | 1)Relief shall be provided with the commissioning of 400KV Patran under Northern Region system strengthening scheme 2) From 400KV Patran,Various 220KV lines such as 400KV Patran -220KV Patran 400KV Patran-220KV Rajla , 400KV Patran-220KV Patiala & 400KV Patran-220KV Mansa DC line which have been planned will provide relief to this section .
8 | 220KV PGCIL- Kartarpur | SC | 0.4 | 106.55 | LILO of 2nd ckt of 400KV PGCIL ,Jalandhar - 220KV Nakodar at 220KV Kartarpur as already planned will reduce the loading .
9 | 220KV PGCIL-KotlaJangan | SC | 0.4 | 103.11
10 | Ablowal-Fagganmajra-1 | DC | 0.4 | 128 | Maximum demand occurred suddenly attributed to load management by Power Controller at that point of time . However normal demand is below the curren carrying capacity of the ACSR conductor Further there will be sufficient relief with the commissioning of 400KV S/Stn Bhalwan .
11 | Ablowal-Fagganmajra-2 | DC | 0.4 | 128
12 | Ablowal-Rajla | SC | 0.4 | 117.9
13 | Ablowal-Patran | SC | 0.4 | 114.3
14 | Sunam-Patran | SC | 0.4 | 99.3
15 | Bahahdurgarh-F.Majra | SC | 0.4 | 128.2
16 | GHTP Lehra | SC | 0.4 | 112.7
17 | Mohali-Lalru | SC | 0.4 | 101.6
18 | Mohali-Sec-80 | SC | 0.4 | 106.7
19 | Malerkotla-Dhuri Ckt-1 | DC | 0.4 | 111.4
20 | Malerkotla-Dhuri Ckt-2 | DC | 0.4 | 111.4
21 | Malerkotla-PGC Ckt-1 | DC | 0.4 | 132.3 | With the erection/commissioning of already planned 220KV PGCIL Malerkotla -220KV Malerkotla link with twin moose conductor will provide relief.
22 | Malerkotla-PGC Ckt-2 | DC | 0.4 | 132.3

## 132KV
LOADING PROFILE OF 132 KV SUB-STATIONS
Sr No. | Name of Substation | Voltage Ratio KV/KV | Trf. Detail No.& MVA | % Loading | Action Plan
1 | 220 KV S/S Baghapurana | 132/11 | 10/12.5 | 96.8 | 1x20 MVA T/F to replace 10/12.5 MVA T/F is already planned vide amendment no-35/12.11.12
2 | 132 KV Badal | 132/66 | 20/25 | 92.44 | 1x40/50 MVA T/F to replace 1x20/25 MVA T/F is already planned vide amendment no-37/16.11.12
|  | 132/66 | 20/25 | 92.44
3 | 132 KV Muktsar | 132/66 | 16/20 | 100 | Matter under Consderation
4 | 132 KV Jalalabad | 132/66 | 12.5/16 | 93.75 | Addl. 25 MVA,132/66 KV is already planned vide Transmission work list 2013-14 at item no-7.
5 | 132 KV Malout | 132/11 | 20 | 95 | Addl. 20 MVA,132/11 KV is already planned vide amendment no-13/22.6.12
6 | 220 KV Mahilpur | 132/11 KV T-1 | 20 | 94 | To give releif to 20 MVA 132/11 KV T/F 6.3/8 MVAis to be augmented to 20 MVA as per planning 2012-13 Amendment no.28 dated 23.2.12
7 | 220 KV Rehana Jattan | 66/11 KV T-1 | 10/12.5 | 97 | Re-adjustment of Feeders is being done.
8 | 132 KV Hoshiapur | 132/11KV T-1 | 12.5/16 | 100 | 1x16/20 MVA T/F to replace 1x12.5/16 MVA T/F is already planned vide amendment no-44/9.1.13.
|  | 132/66-33 KVT-3 | 20/25 | 100 | 1x50 MVA T/F to replace 1x20/25 MVA T/F is already planned vide amendment no-29/21.3.12
|  | 132/66-33KV T-4 | 50 | 100
9 | 132 KV Chohal | 132/66-33KV T-2 | 12.5/16 | 91 | 1x20/25 MVA T/F to replace 1x12.5/16 MVA T/F is already planned vide amendment no-16/11.7.12
10 | 132 KV Nawanshaher | 132/11KV T-1 | 16/20 | 97 | Augumentation of 1x12.5MVA T/F to 1x20 MVA T/F is already planned vide amendment no-38/26.11.12
|  | 132/11KV T-2 | 12.5 | 95
|  | 132/66KV T-3 | 40/50 | 98 | Addl. 1x20/25 MVA T/F is already planned vide amendment no-28/23.2.12
|  | 132/66 KVT-4 | 12.5/16 | 99 | 1x30/40 MVA T/F to replace 1x12.5/16 MVA T/F is already planned vide amendment no-38/26.11.12
11 | 132 KV Banga | 132/11KV T-1 | 16/20 | 95 | 1X20MVA T/F to replace 1x12.5 MVA is already planned vide Transmission work list under new works 2012-13 at item no-13.
12 | 132 KV Jadla | 132/66KV T-2 | 40/50 | 98 | Addl. 25 MVA,132/66 KV is already planned vide Transmission work list 2012-13 at item no-18. (new works)
13 | 220 KV S/S Kartarpur | 66/11 KV | 20 | 91 | Matter under Consderation
14 | 220 KV Jamsher | 66/11KV | 10/12.5 | 92 | Matter under Consderation
15 | 132 KV S/S Nakodar | 132/11KV | 10/12.5 | 94 | Matter under Consderation
16 | 132 KV S/S Urban estate Jalandhar | 132/11KV | 20 | 98 | Matter under Consderation
|  | 132/11KV | 20 | 93 | Matter under Consderation
17 | 132 KV S/S Children park Jalandhar | 132/11KV | 20 | 92 | Matter under Consderation
18 | 220 KV S/S Kohara | 66/11 | 20 | 100 | Matter under Consideration
19 | 132 KV S/S Swadi kalan | 132/11 | 20 | 94 | Addl. 1x12.5 MVA T/F is already planned vide amendment no-15/29.6.12
20 | 220 KV GBR-II | 66/11 | 16/20 | 95 | Matter under Consideration
21 | 132 KV Ghulal | 132/11 | 10/12.5 | 99 | Matter under Consideration
22 | 220 KV Tooran | 66/11 | 20 | 99 | Matter under Consideration
|  | 66/11 | 20 | 99
23 | 220 KV Himmatpura | 66/11 | 12.5 | 96 | Addl. 1x20 MVA T/F is already planned vide amendment no-22/14.8.12
24 | 132 KV Dhariwal | 132/66 | 20/25 | 91.52 | 1x50 MVA T/F to replace 1x20/25 MVA T/F is already planned vide amendment no-44/9.1.13.
25 | 132 KV Verka | 132/66 | 40/50 | 92.9 | Load can be shifted to 220 KV Majitha by suitable links.
|  | 132/11 | 20 | 91.5 | Addl. 1x20 MVA T/F is already planned vide amendment no-1/4.4.2011
26 | 132 KV Naraingarh | 132/66 | 40/50 | 93.7 | load can be shifted to 220 KV S/S Khassa
|  | 132/66 | 20 | 90.25
27 | 220 KV Patti | 66/11 | 20 | 98.25 | Matter under Consideration
28 | 132 KV Bhikhiwind | 132/11 | 10/12.5 | 96.96 | Matter under Consideration
29 | 132 KV Tarn Taran | 132/66 | 40/50 | 91.44 | load can be shifted to 220 KV S/S Rashiana.
30 | 220 KV Chola sahib | 66/11 | 12.5 | 92.32 | Matter under Consideration
31 | 132 KV Batala | 132/66 | 40/50 | 90.6 | Addl. 25 MVA,132/66 KV is already planned vide Transmission work list 2013-14 at item no-2.
32 | 132 KV S.H.G/Pur | 132/66 | 40/50 | 93.62 | Matter under Consideration
33 | 132KV Bathinda-Balluana | SC | 0.2 | 106.45 | Proposed 220KV S/S Badal give relief to overloading.
34 | 132KV Balluana-Gidderbaha | SC | 0.2 | 100.04 | Proposed 220KV S/S Badal give relief to overloading.
35 | 132KV GNDTP Bathinda-IGC Bathinda | SC | 0.2 | 108.76 | Proposed 220KV S/S Talwandi Sabo will give relief to overloading.
36 | 132KV IGC Bathinda-Mour | SC | 0.2 | 109.55 | Proposed 220KV S/S Talwandi Saho will give relief to overloading.
37 | 132KV Mahilpur-Hoshiarpupr | SC | 0.2 | 110.81 | Single Ckt. To double ckt work is near complation
38 | 132 KV Hoshiapur-Bhogpur | SC | 0.2 | 108.75 | Normal demand hence doube Ckt . Line is required .
39 | 132KV Hoshiarpur-Chohal | SC | 0.2 | 109.01 | Temp.M/D due to drawl of load by Hamitpur (H.G). Normal load on Chohal-Hamirpur =150A & Hoshiarpur -Chohal = 250A.
40 | 132KV Kahanpur-Bhogpur | SC | 0.2 | 100 | M/D due to shifting of load . Normal load's 294A. On this day Bhogpur . Alawalpur line was under permit .
41 | 132KV Kahanpur-Jalandhar | SC | 0.2 | 103.88 | M/D due to shifting of load . Normal load's 330A. On this day Bhogpur . Alawalpur line was under permit .
42 | 132KV Jalandhar-Kartarpur | SC | 0.2 | 105.16 | M/D due to shifting of load . Due to Drawl by BBMB Jalandhar Normal load on line is 225A.
43 | 132KV Kapurthala-Kheramandir | SC | 0.2 | 102.86 | Due to commissioning of 220KV S/Stn Kanjli load of 132 KV Sultanpur - Kheramandir-Kapurthala line reduced due to shifting of load fromf 132KV S/Stn Kapurthala. Now normal load on 132KV Kapurthala -Kheramandir is 275A and 132KV Kheramandier-Sultanpur line is 375 A.
44 | 132KV Kheramandir-Sultanpur | SC | 0.2 | 127.22
45 | 132KV BBMB Jalandhar-Urban Esate | SC | 0.2 | 114.4 | To deload 132KV BBMB-Urban Estate -Nakodar line It is proposed either to install 220/132KV 100MVA,220KV S/Stn. Kotla Janga to feed 132KV S/Stn. Nakodar through double Ckt. 7 Km. 132 KV line from Kotla Janga or to feed 66 KV S/Stns .66KV Mehalpur. Parjian being fed presently fro 132KV Nakodar formf 220KV S/Stn. Kotla Janga . By errecting approx. 9 Km link between existing 66KV S/Stn. Shahkot to 66KV S/Stn. Parjain.